## Sheet1
Room Number | Room Name | Equipment Name | Equipment Numbers | Current for each device (A) | Total Equipment Current (A) | Input Voltage (V) | Total Current (A) | Type | Power (kW) | Conductor
100 | Foyer | Lights | 2 | 0.16958 | 0.33917 | 120 | 8.8392 | Electrical | 1.0607 | #14 AWG
|  | FF-1 | 1 | 7.5 | 7.5 | 120
|  | Receptacles | 1 | 1 | 1 | 120
101 | Classroom | Lights | 6 | 0.31667 | 1.9 | 120 | 6.067 | Electrical | 0.72804 | #14 AWG
|  | Receptacles | 4 | 1 | 4 | 120
|  | Sprinkler | 2 | 0.056 | 0.112 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
102 | Closet | Lights | 1 | 0.31667 | 0.31667 | 120 | 1.3167 | Electrical | 0.158 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
103 | Women's Washroom | Lights | 6 | 0.31667 | 1.9 | 120 | 2.955 | Electrical | 0.3546 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
104 | Washroom | Lights | 4 | 0.31667 | 1.2667 | 120 | 2.3777 | Electrical | 0.28532 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
|  | BB-8 | 1 | 25 | 25 | 120 | 25 | Mechanical | 3 | #12 AWG
105 | Corr | Lights | 1 | 0.16958 | 0.16958 | 120 | 1.1696 | Electrical | 0.14035 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
106 | Jan | Lights | 1 | 0.16958 | 0.16958 | 120 | 1.1696 | Electrical | 0.14035 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
107 | Water Meter | Lights | 1 | 0.16958 | 0.16958 | 120 | 1.1696 | Electrical | 0.14035 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
|  | FF-4 | 1 | 7.5 | 7.5 | 120 | 7.5 | Mechanical | 0.9 | #14 AWG
108 | Kitchenette | Lights | 11 | 0.31667 | 3.4833 | 120 | 9.1503 | Electrical | 1.098 | #14 AWG
|  | Receptacles | 5 | 1 | 5 | 120
|  | Sprinkler | 2 | 0.056 | 0.112 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
|  | CCTV | 1 | 0.5 | 0.5 | 120
|  | BB-1 | 1 | 13.75 | 13.75 | 120 | 13.75 | Mechanical | 1.65 | #14 AWG
|  | BB-2 | 1 | 25 | 25 | 208 | 25 | Mechanical | 5.2 | #12 AWG
109 | Commons | Lights | 15 | 1.6417 | 24.625 | 120 | 33.019 | Electrical | 3.9623 | #10 AWG
|  | Receptacles | 7 | 1 | 7 | 120
|  | Sprinkler | 4 | 0.056 | 0.224 | 120
|  | Smoke Detector | 2 | 0.055 | 0.11 | 120
|  | CCTV | 1 | 0.5 | 0.5 | 120
|  | Fire Alarm Horn | 2 | 0.28 | 0.56 | 120
|  | BB-3 | 1 | 25 | 25 | 120 | 25 | Mechanical | 3 | #12 AWG
|  | BB-4 | 1 | 12.5 | 12.5 | 208 | 12.5 | Mechanical | 2.6 | #14 AWG
|  | BB-5 | 1 | 25 | 25 | 120 | 25 | Mechanical | 3 | #12 AWG
|  | BB-9 | 1 | 25 | 25 | 120 | 25 | Mechanical | 3 | #12 AWG
110 | Cultural Activity Room | Lights | 10 | 1.6417 | 16.4167 | 120 | 25.5277 | Electrical | 3.0633 | #12 AWG
|  | Receptacles | 9 | 1 | 9 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
|  | BB-6 | 1 | 21.3 | 21.3 | 208 | 21.3 | Mechanical | 4.4304 | #12 AWG
|  | BB-7 | 1 | 21.3 | 21.3 | 208 | 21.3 | Mechanical | 4.4304 | #12 AWG
|  | CU-1 | 1 | 17.5 | 17.5 | 208 | 17.5 | Mechanical | 3.64 | #14 AWG
|  | CU-2 | 1 | 22.5 | 22.5 | 208 | 22.5 | Mechanical | 4.68 | #12 AWG
|  | CU-3 | 1 | 50 | 50 | 208 | 50 | Mechanical | 10.4 | #6 AWG
|  | CU-4 | 1 | 47.5 | 47.5 | 208 | 47.5 | Mechanical | 9.88 | #8 AWG
111 | Storage | Lights | 1 | 0.16958 | 0.16958 | 120 | 1.1696 | Electrical | 0.14035 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
113 | Information & Gift Shop | Lights | 6 | 0.31667 | 1.9 | 120 | 6.011 | Electrical | 0.72132 | #14 AWG
|  | Receptacles | 4 | 1 | 4 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
114 | Storage (Gift Shop) | Lights | 1 | 0.16958 | 0.16958 | 120 | 1.1696 | Electrical | 0.14035 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
115 | Yukata | Lights | 1 | 0.16958 | 0.16958 | 120 | 1.2806 | Electrical | 0.15367 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
116 | ED Office | Lights | 3 | 0.31667 | 0.95 | 120 | 4.061 | Electrical | 0.48732 | #14 AWG
|  | Receptacles | 3 | 1 | 3 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
117 | Mechanical | Lights | 2 | 0.31667 | 0.63333 | 120 | 3.7443 | Electrical | 0.44932 | #14 AWG
|  | Receptacles | 3 | 1 | 3 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
|  | FF-3 | 1 | 30 | 30 | 120 | 30 | Mechanical | 3.6 | #10 AWG
|  | F-1 | 1 | 12.5 | 12.5 | 208 | 12.5 | Mechanical | 2.6 | #14 AWG
|  | F-2 | 1 | 12.5 | 12.5 | 208 | 12.5 | Mechanical | 2.6 | #14 AWG
118 | Staff | Lights | 2 | 0.16958 | 0.33917 | 120 | 1.4502 | Electrical | 0.17402 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
119 | Admin Office | Light | 4 | 0.31667 | 1.2667 | 120 | 4.3777 | Electrical | 0.52532 | #14 AWG
|  | Receptacles | 3 | 1 | 3 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
120 | Vestibule | Lights | 2 | 0.16958 | 0.33917 | 120 | 1.4502 | Electrical | 0.17402 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
|  | FF-2 | 1 | 30 | 30 | 120 | 30 | Mechanical | 3.6 | #10 AWG
|  | EF-2 | 1 | 8.75 | 8.75 | 208 | 8.75 | Mechanical | 1.82 | #14 AWG
121 | Classroom | Lights | 6 | 0.31667 | 1.9 | 120 | 3.011 | Electrical | 0.36132 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
122 | Exhibit Gallery | Lights | 10 | 0.31667 | 3.1667 | 120 | 8.2777 | Electrical | 0.99332 | #14 AWG
|  | Receptacles | 5 | 1 | 5 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
123 | Tea Ceremony | Lights | 1 | 0.31667 | 0.31667 | 120 | 1.4277 | Electrical | 0.17132 | #14 AWG
|  | Receptacles | 1 | 1 | 1 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
200 | Stair | Lights | 2 | 0.097837 | 0.19567 | 120 | 0.19567 | Electrical | 0.023481 | #14 AWG
203 | Mechanical | Lights | 20 | 0.31667 | 6.3333 | 120 | 20.0443 | Electrical | 2.4053 | #12 AWG
|  | Receptacles | 13 | 1 | 13 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
|  | Keypad | 1 | 0.1 | 0.1 | 120
|  | CCTV | 1 | 0.5 | 0.5 | 120
|  | EF-1 | 1 | 7.5 | 7.5 | 120 | 7.5 | Mechanical | 0.9 | #14 AWG
|  | DHWT-1 | 1 | 6.25 | 6.25 | 120 | 6.25 | Mechanical | 0.75 | #14 AWG
204 | Telecom | Lights | 6 | 0.31667 | 1.9 | 120 | 9.091 | Electrical | 1.0909 | #14 AWG
|  | Receptacles | 7 | 1 | 7 | 120
|  | Sprinkler | 1 | 0.056 | 0.056 | 120
|  | Smoke Detector | 1 | 0.055 | 0.055 | 120
|  | Wireless Access Point | 1 | 0.08 | 0.08 | 120
94.8235

## Sheet3
CU | Condensing unit
F | Furnace
DHWT | Domestic Hot Water Tank
EF | Exxhaust Fan
BB | Baseboard Heater
FF | Forceflow Fan