## Table 1
MECHANICAL EQUIPMENT SCHEDULE Printed on Feb 17, 2023 at 1:48 PM
Unit No. | Description | Location | Nameplate |  |  |  | Overcurrent Protection |  |  | Feeder |  |  | Fed From | Disconnect |  |  |  | Starter/VFD |  |  |  |  | Starter Control | [6 empty] | Remarks
|  |  | Voltage (V) | Phase Ø | MCA (A) | Load (HP, FLA, kW) | Type | Rating | Poles | Conductors | Bond | Conduit |  | NEMA Rating | S | I | C | Type | NEMA Size | S | I | C | Type | Remote Type | N/O Contacts | N/C Contacts | S | I | C
AIR CONDITIONING EQUIPMENT
CU-1 | CONDENSING UNIT | EXTERIOR - SOUTH CULTURAL ACTIVITY | 208 | 3 | 14 | 14.0 FLA | CB | 30 | 3 | cu |  | 8 | [10 empty] | INT | [6 empty] | CONTROLLED BY FURNACE
CU-2 | CONDENSING UNIT | EXTERIOR - SOUTH CULTURAL ACTIVITY | 208 | 3 | 22.5 | 18 | CB | 45 | 3 | cu |  | 6 | [10 empty] | INT | [6 empty] | CONTROLLED BY FURNACE
CU-3 | CONDENSING UNIT | EXTERIOR - SOUTH CULTURAL ACTIVITY | 208 | 3 | 47.5 | 39 | CB | 90 | 3 | cu |  | 1 | [10 empty] | INT | [6 empty] | CONTROLLED BY FURNACE
CU-4 | CONDENSING UNIT | EXTERIOR - SOUTH CULTURAL ACTIVITY | 208 | 3 | 92.5 | 37 | CB | 90 | 3 | cu |  | 2 | [10 empty] | INT | [6 empty] | CONTROLLED BY FURNACE
AIR HANDLING
F-1 | FURNACE | MECHANICAL ROOM 117 | 208 | 3 | 12.5 | 10.0 FLA | CB | 25 | 3 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
F-2 | FURNACE | MECHANICAL ROOM 117 | 208 | 3 | 12.5 | 10.0 FLA | CB | 25 | 3 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
F-3 | FURNACE | MECHANICAL ROOM 203 | 208 | 3 | 12.5 | 10.0 FLA | CB | 25 | 3 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
F-4 | FURNACE | MECHANICAL ROOM 203 | 208 | 3 | 15 | 12.0 FLA | CB | 30 | 3 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
DOMESTIC HOT WATER
DHWT-1 | DOMESTIC HOT WATER TANK | MECHANICAL ROOM 203 | 120 | 1 | 6.25 | 5.0 FLA | CB | 15 | 1 | cu |  | 14 | [10 empty] | INT
EXHAUST FANS
EF-1 | EXHUAST FAN | MECHANICAL ROOM 203 | 120 | 1 | 3.8 | 0.25 HP | CB | 15 | 1 | cu |  | 14 | [10 empty] | COMB | [6 empty] | INTERLOCK LOCAL LIGHTING
EF-2 | EXHUAST FAN | ROOM 120 | 208 | 3 | 8.7 | 1.5 HP | CB | 20 | 3 | cu |  | 12 | [10 empty] | VFD | [6 empty] | INTERLOCK LOCAL LIGHTING
BASEBOARD HEATERS
BB-1 | BASEBOARD HEATER | KITCHENETTE 108 | 208 | 1 | 12.02 | 2.5 kW | CB | 30 | 2 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
BB-2 | BASEBOARD HEATER | KITCHENETTE 108 | 120 | 1 | 10 | 1.0 kW | CB | 20 | 1 | cu |  | 12 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
BB-3 | BASEBOARD HEATER | COMMONS 109 | 120 | 1 | 10 | 1.0 kW | CB | 20 | 1 | cu |  | 12 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
BB-4 | BASEBOARD HEATER | COMMONS 109 | 208 | 1 | 12.02 | 2.5 kW | CB | 30 | 2 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
BB-5 | BASEBOARD HEATER | COMMONS 109 | 120 | 1 | 10 | 1.0 kW | CB | 20 | 1 | cu |  | 12 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
BB-6 | BASEBOARD HEATER | CULTURAL ACTIVITY 110 | 208 | 1 | 12.02 | 2.5 kW | CB | 30 | 2 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
BB-7 | BASEBOARD HEATER | CULTURAL ACTIVITY 110 | 208 | 1 | 12.02 | 2.5 kW | CB | 30 | 2 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
BB-8 | BASEBOARD HEATER | MENS 104 | 120 | 1 | 10 | 1.0 kW | CB | 20 | 1 | cu |  | 12 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
BB-9 | BASEBOARD HEATER | COMMONS 109 | 120 | 1 | 10 | 1.0 kW | CB | 20 | 1 | cu |  | 12 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
FORCE FLOWS
FF-1 | FORCE FLOW FAN | FOYER 100 | 120 | 1 | 7.5 | 6.0 FLA | CB | 15 | 1 | cu |  | 14 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
FF-2 | FORCE FLOW FAN | ROOM 120 | 120 | 1 | 15 | 1.5 kW | CB | 30 | 1 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
FF-3 | FORCE FLOW FAN | MECHANICAL ROOM 117 | 120 | 1 | 15 | 1.5 kW | CB | 30 | 1 | cu |  | 10 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
FF-4 | FORCE FLOW FAN | WATER METER 107 | 120 | 1 | 7.5 | 6.0 FLA | CB | 15 | 1 | cu |  | 14 | [10 empty] | LTST | [6 empty] | CONTROLLED BY THERMOSTAT
ZERO CARBON INITIATIVES
| EV CHARGING | OUTSIDE BUILDING | 120 | 1 | 16.25 | 1.5KW | CB | 35 | 1 | cu |  | 8
COMMON ABBREVIATIONS E=ELECTRICAL CONTRACTOR M=MECHANICAL CONTRACTOR INT=INTEGRAL TO UNIT (BY MANUFACTURER) S=SUPPLIED BY I=INSTALLED BY C=CONNECTED BY NR=NOT REQUIRED NAMEPLATE & FEEDER ABBREVIATIONS FLA=FULL LOAD AMPACITY MCA=MINIMUM CIRCUIT AMPACITY HP=HORSE POWER FU=FUSE(S) P=POLES STARTER TYPE ABBREVIATIONS VFD=VARIABLE FREQUENCY DRIVE MAG=MAGNETIC FVNR MAN=MANUAL COM=COMBO BREAKER + MAG FVNR=FULL VOLTAGE NON-REVERSING FVR=FULL VOLTAGE REVERSING SOFT=SOFT STARTER TST=LINE VOLTAGE THERMOSTAT STARTER CONTROL TYPE ABBREVIATIONS BMS=BUILDING MANAGEMENT SYSTEM H,O,A=HAND,OFF,AUTO F,O,R=FORWARD,OFF,REVERSE O,O=ON,OFF LTST=LOW VOLTAGE THERMOSTAT R,J=RUN,JOG F,R=FORWARD,REVERSE O,C=OPEN,CLOSE
GENERAL NOTES REFERRAL NOTES a. IN MOST CASES THE FLA'S AND ASSOCIATED BRANCH CIRCUITS ARE BASED ON THE CANADIAN ELECTRICAL CODE. CONFIRM THE ACTUAL FLA'S OF MOTORS WITH THE MECHANICAL CONTRACTOR [1] - PRIOR TO ORDERING EQUIPMENT (BREAKERS, OVERLOADS, ETC.), AND INSTALLATION OF BRANCH CIRCUITS. APPROVAL OF DISTRIBUTION SHOP DRAWINGS IS BASED ON THE ASSUMPTION THAT FLA'S OF MOTORS HAVE BEEN CONFIRMED. NO ADDITIONAL COSTS WILL BE CONSIDERED FOR FAILURE TO CONFIRM THE FLA'S OF MOTORS PRIOR TO SUBMISSION OF DISTRIBUTION EQUIPMENT [2] - SHOP DRAWINGS. [3] - b. IF MOTOR FEEDER SIZES ARE NOT SHOWN, REFER TO SINGLE LINE DIAGRAM. c. ELECTRICAL CONTRACTOR IS TO UPDATE ALL INFORMATION IN THIS SCHEDULE PRIOR TO SUBMITTING AS-BUILT DRAWINGS. THE OVERCURRENT PROTECTION AND MOTOR NAMEPLATE COLUMNS ARE TO BE FILLED IN BY THE CONTRACTOR. d. WHERE INDICATED, PROVIDE ROOFTOP GFCI RECEPTACLES AS PER CEC RULE 26-704. e. UNLESS NOTED OTHERWISE, ALL EQUIPMENT TEMPERATURE RATINGS ARE ASSUMED TO BE 75°C (CONDUCTOR TEMPERATURE). FOR EXISTING EQUIPMENT, CONFIRM THAT THE TEMPERATURE RATINGS ARE 75°C. IF THE EQUIPMENT IS UNMARKED AND RATED 100 A OR LESS, ASSUME THE TEMPERATURE RATING IS 60°C AND INCREASE THE CONDUCTOR SIZE APPROPRIATELY (CEC RULE 4- 006).